## Sheet1
Proposed Construction of Food Processing Unit For Production of Prasad Ladu on Gat No 87-88 At Nimgaon Korhale Tal- Rahata.
S. NO | Description | Qty | Unit | Rate | Amount
A | Civil Work
1 | Designing, Detailing, supplying, installing, profiling, Stressing And Cement Grouting For Bonded Type Post Tensioning (PT) Work With HT Strands Of Approved Make Conforming To IS14268-1995 For Following Items. Rate shall be inclusive of supplying of HT strandsand sheathing (Galvalum ecorrugated ducts) of approved make, decoiling the strands, cutting th esametor equired lengths and laying of HT strands, in serting the strands, profiling, fixing live end anchor ages including the supply of stressing anchorages, casting, barrels, wedges, end plates suitable for Tendons, vents fo rgrout, making dead end anchorages including flowering the strands, fixingt end on support bars, supervising and fixing of anti bursting reinforcement, stressing the cables, end trimming, grouting the cables with cement and admixtures, strip painting at strand locations, including necessary materials, accessories, Plant & Machineries, tools and tackles, scaffolding, consumables etc., obtaining design approvals from consultant for the work etc with all lifts and leads complete. Spec.No. : As Directed By Engineer In Charge.
| FIRST FLOOR | 1535.2 | Sqm | 924.15 | 1418755.08
2 | Roofing:- Providing and fixing Colour Coated 0.5 mm Thick Galvalume Roofing Sheet Of High Tensile (min 550 MPa in Yield strength) & fixing with with self drilling screws with necessery overlaping, ridge, hip or valley or eaves board & fecia and all trims, gutters and necessery provision to close & protect shet egder including fixing with approved self tapping screws, nut bolt and EPDM washers and scaffolding etc. Complete. Spec. No. As Directed By Engineer In Charge.
| FIRST FLOOR | 560 | Sqm | 909 | 509040
3 | Wall Cladding:- Providing and fixing 50 mm Thick PUF Panel Sandwitched Profiled Colour Coated Galvalume Wall Cladding Sheet of High Tensile (min 550 MPa in Yield strength) with top G.I. sheet 0.4mm thick & bottem G.I. sheet 0.3mm thick & PUF density 40 Kg / Cum (+ / - 2 Kg / Cum) sandwitched in between top & bottem G.I. sheet & fixing with with self drilling screws with necessery tongue and groove jointer, ridge, hip or valley or eaves board & fecia and all trims, gutters and necessery provision to close & protect shet egder, with necessery cutting of windows / doors and opning as per opning schedule, including fixing with approved self tapping screws, nut bolt and EPDM washers and scaffolding, Puf Panel Rolling Shutter, etc. Complete. Spec. No. As Directed By Engineer In Charge.
| GROUND FLOOR | 456.46 | Sqm | 2500 | 1141150
| FIRST FLOOR | 543.44 | Sqm | 2525 | 1372186
4 | Providing and fixing 25 mm Thick Heat Insulation Sheet Aproved Colour And Approved Make Below Roofing, including necessary farming, all required accessories and labour etc. complete Spec. No. As directed by Engineer in charge.
| GROUND FLOOR | 560 | Sqm | 454.5 | 254520
5 | Providing & applying of a 4 Component, Single Layer, Seamless, Solvent-Free, Moisture Insensitive And Food-Safe Polyurethane Concrete Flooring System of density more than 1950 kg/cu.mtr to have a smooth & even matt finish matching below mentioned performance properties: 1):- Mixed density more than 1900kg/cu.mtr. 2):- Abrasion resistance class of AR0.5 as per BS 8204-2. 3):- Cleanable to standards of Stainless steel. 4):- Zero Absorption as per CP.BM2/67/2. 5):- Static Modulus of Elasticity of 3.3x10^3 Mpa and Toughness of 96.7x10^3 Mpa as per Modified ASTM C469/C469M. 6):- Coefficient of thermal expansion of 3.6 x 10^-5 /oC as per ASTM C531. 7):- Shore D hardness of 80. 8):- Tensile strength of >7Mpa. 9):- Flexural strength of >20Mpa. 10):- Adhesion to concrete of more than 2Mpa or until concrete fails. 11):- Slip resistance classification 35 as per EN13036-4 12):- Fire resistance classification of Bfl-S1 as per EN 13501-1:2002. 13):- Surface spread of flame of CLASS 2 as per BS476, Part 7. 14):- Cure time of 12 hours for foot traffic and 24 hours for vehicular traffic at 30 degree Centi Grade. Applied At A Thickness Of 3mm Over A 1mm Scratch Coat of the same material by an authorised applicator of the manufacturer in accordance to the application guideline as provided by the manufacturer. Spec. No. As directed by Engineer in charge. |  |  |  | 0
| GROUND FLOOR | 2690.6 | Sqm | 2200 | 5919320
6 | Providing & applying of a Smooth 50 mm x 50mm Coving At Junctions Of Floor And Wall Using A Polyurethane Concrete Moisture insensitive coving mortar matching the following performance requirement; 1):- Moisture tolerant. 2):- Zero Absorption as per CP.BM2/67/2. 3):- Density > 2000 kg / cu. mtr. 4):- Flexural Strength >15Mpa as per EN 13892 part 2. Applied over a polyurethane primer including surface preparation. Spec. No. As directed by Engineer in charge. |  |  |  | 0
| GROUND FLOOR | 721.97 | Rmt | 506 | 365316.82
7 | Providing and applying of a 2 Component Polyurethane Sealant At Construction Joints Of Same Colour As The Floor Matching the following performance parameters; 1):- Density – 1550 – 1600 kg/cu.mtrs. 2):- Tensile Strength – 1.6-2.0 Mpa (ISO R527). 3):- Elongation at break – 205-32% (ISO R 527). 4):- Hardness (DIN 53505) Shore A – ca 80. Spec. No. As directed by Engineer in charge.
| GROUND FLOOR | 721.97 | Rmt | 202 | 145837.94
8 | Providing and applying Poly Urithine (PU) Paint Of Approved Quality, Colour And Shade To New Surface In Two Coats including scaffolding, preparing the surface. (excluding primer coat) etc. complete. Spec. No. As directed by Engineer in charge.
| GROUND FLOOR | 2191.12 | Sqm | 250 | 547780
| FIRST FLOOR | 4702 | Sqm | 252.5 | 1187255
9 | Providing and Fixing Acrylic Name Board On Provided Base Of Composite Aluminum Panel In Letter Size 450 X 450 mm And 25mm Thick In English Or Marathi of approved color and finish in line and level, Including all fixing asseccories, Drilling, Fabricating, Scaffolding all labour etc. complete. Spec. No. As directed by Engineer in Charge.
| FIRST FLOOR | 5.7 | Sqm | 5050 | 28785
10 | Providing and Fixing Acrylic Signage Board On Provided Base Of Aluminum Panel Sheet English Or Marathi of approved color and finish in line and level, Including all fixing asseccories, Drilling, Fabricating, Scaffolding all labour etc. complete. Spec. No. As directed by Engineer in Charge.
| GROUND FLOOR | 33.76 | Sqm | 2000 | 67520
11 | Providing And Paisting Mural Art Wall Painting of approved Quality and finish in line and level, Including all fixing asseccories, Scaffolding And all Labour etc. complete. Spec. No. As directed by Engineer in Charge.
| FIRST FLOOR | 18 | Sqm | 30300 | 545400
12 | Providing and fixing in position PVC Drain Channel For Floor Drain Size Of Length 500mm Width 200mm And Depth 175mm With And Reinforced PVC Grid Cover Size Of Length 500mm Width 200mm with necessary fixtures and fitting including making joint & necessary fittings and tested etc. complete. Spec. No. As directed by Engineer in charge. ( ASTRAL CAT. NO. CSA200 AND CGRN20SG )
| GROUND FLOOR | 243.51 | Rmt | 1400 | 340914
|  | Total Civil works Amt (A) |  |  | 13843779.84
B | FIRE FIGHTING
13 | PUMP (Electrically Driven)
Supplying, installing, testing & commissioning of electric driven, suitable for autometic operation of horizontal single stage centrifugal type synchoronous speed of 2900 rpm, TEFC conforming to IP-55 & flexible coupling gaurd mounted on a common structural base plate with 150mm dia gun metal pressure gauges with isolation cock and piping, suitable vibration elimination pads of approved design for pump foundation, motor to be suitable for 415 volts, 3 phase, 50 cycles AC.Pump shall be designed in such a way that any case drop in the pressure main fire or diesel pump/Pump will be started automatically and there shall be provision of to run the pump in auto as well as manual mode.
| Capacity 2280 LPM at 7 Kg/cm2 delivery pressure for Fire Hydrant / Sprinkler Network. | 1 | Each | 175000 | 175000
14 | Pumps (Diesel) Engine Driven | 1 | Each | 320000 | 320000
Supplying, installing, testing and commissioning of horizontal single stage centrifugal pumping set with CI volute and bronze impeller with mechanical seals directly coupled to automatic Diesel Engine complete with all ccessories like self starting by means of Battery powered electric starter motor, oil bath air cleaner, exhaust silencer etc. complete in all respects. The engine & the pump will be mounted on common base plate on anti-vibration mountings 2200 LPM-56 MTR Head
15 | Control Panel (Engine Driven Pump) | 1 | Set | 50000 | 50000
Supplying, erecting, testing and commissioning cubicle pattern electrical control panel (out door) made of 14 SWG MS sheet duly painted with powder coated comprising of the following:
24 Volts 120 AH capacity battery set.
15 Amps battery charger with Tricke and boost facility.
0-32 Volts votlmeter.
0-15 Amps ammeter.
Auto-starting contactor with relay.
Auto/Manual selector switch with push button for manual start.
16 | Oil Tank | 1 | Set | 18500 | 18500
Supplying, fixing and commissioning 500 ltrs. capacity including first fill of 500 ltrs high speed diesel oil in 16 SWG MS steel oil tank with manhole cover, glass gauge, inlet and outlet connections with gate valves, drain plug, GI piping between tank and engine vent pipe with wire mesh etc. duly painted and mounted on suitable MS angle staging to maintain gravity flow of oil.
17 | Exhaust Piping | 1 | Rmt | 2500 | 2500
Supplying, erecting and commissioning additional exhaust piping with heat resistance asbestos rope insulation wrapped all along the pipe including a cowl at the top with necessary MS clamps on walls/ceiling.
18 | Fire Pump Panel (Electrical) | 1 | Set | 150000 | 150000
Suppling, erecting, testing and commissioning cubicle pattern electrical control panel made of 14 SWG MS Sheet duly painted with enamel paint, comprising of the following:
Incoming
1 No, 400Amps FP MCCB (50 KA)
Bus Bars
1 Set 3 Phase, 4 wire busbar 400 Amps Aluminium conductor, duly sleeved in PVC colour coded sleeves.
Outgoings
2 Nos 150 A TP MCCB withneutral link (25 KA)
1 Nos 63 A TP MCCB with neutral link (25 KA)
2 No. Star Delta starter with overload relay suitable for 70 HP.
1 No. Dol starter with overload relay suitable for 10 HP.
Metering
1 Set RYB phase indication lamps with toggle suitable and protection fuses.
1 No. 0-500 volts, 96mm square with with MCB.
1 No. 0-400 Amps Ammeter of 96mm square with CT's
1 No. 96sqmm energy meter with CT's
19 | Supplying and installing 32 mm GI C Class ERW Pipe | 1 | Rmt | 418 | 418
20 | Supplying and installing 40 mm GI C Class ERW Pipe | 1 | Rmt | 460 | 460
21 | Supplying and installing 65 mm GI C Class ERW Pipe | 1 | Rmt | 650 | 650
22 | 150mm dia. Installation Control Valve assembly comprissing of vertical wet alarm valve, including the cost of 150 mm dia butterfly valve, hydraulic alarm motor & gong, 15mm dia. Test valve, 50mm dia. Drain valve and all necessary trimming connections including 2 nos. pressure gauges as per manufacturer's catalogue (UL / FM approved ). | 1 | Each | 30000 | 30000
| Total Amount of Mechanical works (B) |  |  |  | 747528
C | INTERNAL, EXTERNAL ELECTRIFICATION
23 | 10W LED Mirror light of Wipro Make Cat No. D531065 GARNET BATTEN | 1 | Each | 600 | 600
24 | Supplying and fixing 32A 3∅ Industrial Power Socket with enclosure | 1 | Each | 3500 | 3500
25 | Supplying and fixing 20A 1∅ Industrial Power Socket with enclosure | 1 | Each | 3200 | 3200
26 | Supply installation testing and commissiong of 6 W public area ceiling speakers 85 dBA @ 3m @ lowest setting complete with GI backboX. | 1 | Each | 2400 | 2400
27 | MAIN LT PANEL
| Supplying, installing, testing and commissioning cubicle type free floor mounted front operated panels made out of 14 SWG powder coated sheet steel, PVC colour coded aluminium bus bar, 75 x 6 Sq.mm aluminium earth tape from end to end of the panel, consisting of the following, all as per single line diagram. (G.A. drawing of panel to be approved before fabrication) Site inspection required before despatching the panel at site. | 1 | Each | 390000 | 390000
All Incoming and Outgoing ACBs/MCCB's shall have Ics=Icu=Icw=95/65/50/35/25KA minimum having microprocessor based release trip with O/C, S/C, E/F protection and ON/OFF/TRIP indication for each.
All MCCB's shall have with rotary operating mechanism and ON/OFF indication for each.
Incoming
1000 Amps, 415 Volts, 4 Pole, 50Hz, ACB 50KA
Bus bars
1 Set of 1000 Amps, 415 Volts, 50 Hz, 3 phase, 4 wire colour coded Al. bus bars.
Instruments
1 No 0-500 Volts, Digital voltmeter with built in selector switch and protection fuses.
1 No 0-1000 Amps, Digital ammeter with built in selector switch and matching CT's .
1 Set of RYB phase indicating lamps (LED).
1 Set red & green (ON, OFF) indicating lamps (LED) for incomer.
1 Set of multification KWH meter (Suitable CT/PT)
Outgoing
02 Nos.315A TP MCB,35 KA
01 Nos.200A TP MCB,25 KA
01 Nos.160A TP MCB,25 KA
02 Nos.100A TP MCB,25 KA
04 Nos. 63A TP MCB, 10 KA
01 Nos. 50A TP MCB, 10 KA
01 Nos. 40A TP MCB, 10 KA
02 Nos. Vaccant
02 Nos. Spare
28 | Supplying, installing, testing and commissioning cubicle type free floor mounted front operated panels made out of 14 SWG powder coated sheet steel, PVC colour coded aluminium bus bar, 75 x 6 Sq.mm aluminium earth tape from end to end of the panel, consisting of the following, all as per single line diagram. (G.A. drawing of panel to be approved before fabrication) Site inspection required before despatching the panel at site. | 1 | Each | 98000 | 98000
All Incoming and Outgoing ACBs/MCCB's shall have Ics = Icu = Icw = 95 / 65 / 50 / 35 / 25KA minimum having microprocessor based release trip with O/C, S/C, E/F protection and ON/OFF/TRIP indication for each.
All MCCB's shall have with rotary operating mechanis and ON/OFF indication for each.
Incoming
160 Amps, 415 Volts, 4 Pole, 50Hz, MCCB 25KA
Bus bars
1 Set of 160 Amps, 415 Volts, 50 Hz, 3 phase, 4 wire colour coded Al. bus bars.
Instruments
1 No 0-500 Volts, Digital voltmeter with built in selector switch and protection fuses.
1 No 0-160 Amps, Digital ammeter with built in selector switch and matching CT's .
1 Set of RYB phase indicating lamps (LED).
1 Set red & green (ON, OFF) indicating lamps (LED) for incomer.
1 Set of multification KWH meter (Suitable CT/PT)
Outgoing
01 Nos.63A TP MCB,10 KA
05 Nos.40A TP MCB,10 KA
06 Nos.32A TP MCB,10 KA
02 Nos. Spare
29 | CAPACITOR PANEL (150 KVAR) | 1 | Each | 150000 | 150000
Incoming
01 Nos. 250 Amps, TP MCCB 35KA
Bus bar
1 set of 250 Amps, 415 volts, 50 Hz, 3 phase, 4 wire colour coded aluminium bus bars.
Outgoing
02 Nos. 125 Amps, TP MCCB with isolable neutral
01 Nos. 70 Amps, TP MCB with isolable neutral
01 Nos. 50 Amps, TP MCB with isolable neutral
03 Nos. 32 Amps, TP MCB with isolable neutral
02 Nos. 50 KVAR 3 phase 415 V capacitor
01 Nos. 25 KVAR 3 phase 415 V capacitor
01 Nos. 10 KVAR 3 phase 415 V capacitor
03 Nos. 5 KVAR 3 phase 415 V capacitor
1 set red & green (on/off) indication for each contactor.
Sets on/off push buttons for manual operation
1 No. 12-14 stage APFCR and allied control wiring in-built power factor meter.
1 No. automanual selector switch.
Note- Each capacitor bank shall have facility of switiching on individually in manual mode independent of APCR relay or in auto mode through APCR relay. Few contactor shall be kept for fixed operation.
30 | External Lighting DB (Feeder Pilar) | 1 | Each | 60000 | 60000
Incoming
1 No. 63 Amps, FP RCBO, 415 volts, 3 phase, 50 Hz (100 mA Sensitivity).
1 No. 60 Amps, FP contactor with auxiliary contacts. The contactor to be controlled by Timer through an Auto/Manual Selector switch. Timer shall be 24 hrs programmable.
Outgoing
4 Nos 32 Amps, TPN MCB, 415 volts, 3 phase, 50 Hz.
Bus bar
1 set 63 Amps, 415 volts, 3 phase 4 wire colour coded copper bus bars.
Neutral Link
Suitable for above outgoings separate for each phase.
Earthing Bus
Suitable for above outgoings separate for each phase.
LIGHTING ARRESTER
31 | Supply, installation, testing of Transducer type Building lightning arrester "EARLY STREAMER" to cover protection radius of 65.0 mtr. with 5mtr stem and fixing arrangement. (Indelec or Eqvt.). Required installation/ mounting details shall be submitted prior to installation. | 1 | NOS. | 216375 | 216375
32 | Supply, Installation, testing of Copper 5 spikes Building lightning arrester with stem and fixing arrangement. | 1 | NOS. | 22910 | 22910
33 | Supply, installation, testing of disconnecting link box for lightning down conductor at 1 mtr. from GL with SMC insulator and Gunmetal 50 x 6 mm disconnecting link. | 1 | NOS. | 4667 | 4667
CC TV SURVEILLANCE
34 | Supply, Installation, Testing & Commissioning of 1/3", CCD type, Indoor application Colour Dome camera with 540 TVL and lens 4 to 9 mm focal lens, viewing angle wide Wide: 98.5º x 75.3º (H x V). | 1 | NOS. | 7200 | 7200
35 | Supply, installation, testing & commissioning 4 channel Digital Video Recorder with capacity of 1TB built in Hard disk, and same shall be having the capacity to have analog and SVGA output, shall be with TCP/ IP connectivity. | 1 | NOS. | 17200 | 17200
36 | Supply, installation, testing & commissioning of 21" Hi resolution Colour Monitor | 1 | NOS. | 13300 | 13300
37 | RG 59 Coaxial Video Cable in 19mm PVC conduit with all accessories. | 1 | Rmt | 65 | 65
38 | Supply and laying of 3 Core x 1.5 Sq.MM copper conductors, power cable in 19mm dia PVC conduits for Power Supply for the Dome Cameras. | 1 | Rmt | 110 | 110
| Total Amount of Electrical works (c) |  |  |  | 989527
| TOTAL AMOUNT (A+B+C) |  |  |  | 15580834.84

## BOQ
Proposed Construction of Food Processing Unit For Production of Prasad Ladu on Gat No 87-88 At Nimgaon Korhale Tal- Rahata.
S. NO | Description | Quantity | Unit | Rate | Amount
A | Civil Work
1 | Designing, Detailing, supplying, installing, profiling, Stressing And Cement Grouting For Bonded Type Post Tensioning (PT) Work With HT Strands Of Approved Make Conforming To IS14268-1995 For Following Items. Rate shall be inclusive of supplying of HT strandsand sheathing (Galvalum ecorrugated ducts) of approved make, decoiling the strands, cutting th esametor equired lengths and laying of HT strands, in serting the strands, profiling, fixing live end anchor ages including the supply of stressing anchorages, casting, barrels, wedges, end plates suitable for Tendons, vents fo rgrout, making dead end anchorages including flowering the strands, fixingt end on support bars, supervising and fixing of anti bursting reinforcement, stressing the cables, end trimming, grouting the cables with cement and admixtures, strip painting at strand locations, including necessary materials, accessories, Plant & Machineries, tools and tackles, scaffolding, consumables etc., obtaining design approvals from consultant for the work etc with all lifts and leads complete. Spec.No. : As Directed By Engineer In Charge.
| FIRST FLOOR | 1535.2 | Sqm
2 | Roofing:- Providing and fixing Colour Coated 0.5 mm Thick Galvalume Roofing Sheet Of High Tensile (min 550 MPa in Yield strength) & fixing with with self drilling screws with necessery overlaping, ridge, hip or valley or eaves board & fecia and all trims, gutters and necessery provision to close & protect shet egder including fixing with approved self tapping screws, nut bolt and EPDM washers and scaffolding etc. Complete. Spec. No. As Directed By Engineer In Charge.
| FIRST FLOOR | 560 | Sqm
3 | Wall Cladding:- Providing and fixing 50 mm Thick PUF Panel Sandwitched Profiled Colour Coated Galvalume Wall Cladding Sheet of High Tensile (min 550 MPa in Yield strength) with top G.I. sheet 0.4mm thick & bottem G.I. sheet 0.3mm thick & PUF density 40 Kg / Cum (+ / - 2 Kg / Cum) sandwitched in between top & bottem G.I. sheet & fixing with with self drilling screws with necessery tongue and groove jointer, ridge, hip or valley or eaves board & fecia and all trims, gutters and necessery provision to close & protect shet egder, with necessery cutting of windows / doors and opning as per opning schedule, including fixing with approved self tapping screws, nut bolt and EPDM washers and scaffolding, Puf Panel Rolling Shutter, etc. Complete. Spec. No. As Directed By Engineer In Charge.
| GROUND FLOOR | 456.46 | Sqm
| FIRST FLOOR | 543.44 | Sqm
4 | Providing and fixing 25 mm Thick Heat Insulation Sheet Aproved Colour And Approved Make Below Roofing, including necessary farming, all required accessories and labour etc. complete Spec. No. As directed by Engineer in charge.
| GROUND FLOOR | 560 | Sqm
5 | Providing & applying of a 4 Component, Single Layer, Seamless, Solvent-Free, Moisture Insensitive And Food-Safe Polyurethane Concrete Flooring System of density more than 1950 kg/cu.mtr to have a smooth & even matt finish matching below mentioned performance properties: 1):- Mixed density more than 1900kg/cu.mtr. 2):- Abrasion resistance class of AR0.5 as per BS 8204-2. 3):- Cleanable to standards of Stainless steel. 4):- Zero Absorption as per CP.BM2/67/2. 5):- Static Modulus of Elasticity of 3.3x10^3 Mpa and Toughness of 96.7x10^3 Mpa as per Modified ASTM C469/C469M. 6):- Coefficient of thermal expansion of 3.6 x 10^-5 /oC as per ASTM C531. 7):- Shore D hardness of 80. 8):- Tensile strength of >7Mpa. 9):- Flexural strength of >20Mpa. 10):- Adhesion to concrete of more than 2Mpa or until concrete fails. 11):- Slip resistance classification 35 as per EN13036-4 12):- Fire resistance classification of Bfl-S1 as per EN 13501-1:2002. 13):- Surface spread of flame of CLASS 2 as per BS476, Part 7. 14):- Cure time of 12 hours for foot traffic and 24 hours for vehicular traffic at 30 degree Centi Grade. Applied At A Thickness Of 3mm Over A 1mm Scratch Coat of the same material by an authorised applicator of the manufacturer in accordance to the application guideline as provided by the manufacturer. Spec. No. As directed by Engineer in charge.
| GROUND FLOOR | 2690.6 | Sqm
6 | Providing & applying of a Smooth 50 mm x 50mm Coving At Junctions Of Floor And Wall Using A Polyurethane Concrete Moisture insensitive coving mortar matching the following performance requirement; 1):- Moisture tolerant. 2):- Zero Absorption as per CP.BM2/67/2. 3):- Density > 2000 kg / cu. mtr. 4):- Flexural Strength >15Mpa as per EN 13892 part 2. Applied over a polyurethane primer including surface preparation. Spec. No. As directed by Engineer in charge. |  |  | 0 | 0
| GROUND FLOOR | 721.97 | Rmt
7 | Providing and applying of a 2 Component Polyurethane Sealant At Construction Joints Of Same Colour As The Floor Matching the following performance parameters; 1):- Density – 1550 – 1600 kg/cu.mtrs. 2):- Tensile Strength – 1.6-2.0 Mpa (ISO R527). 3):- Elongation at break – 205-32% (ISO R 527). 4):- Hardness (DIN 53505) Shore A – ca 80. Spec. No. As directed by Engineer in charge.
| GROUND FLOOR | 721.97 | Rmt
8 | Providing and applying Poly Urithine (PU) Paint Of Approved Quality, Colour And Shade To New Surface In Two Coats including scaffolding, preparing the surface. (excluding primer coat) etc. complete. Spec. No. As directed by Engineer in charge.
| GROUND FLOOR | 2191.12 | Sqm
| FIRST FLOOR | 4702 | Sqm
9 | Providing and Fixing Acrylic Name Board On Provided Base Of Composite Aluminum Panel In Letter Size 450 X 450 mm And 25mm Thick In English Or Marathi of approved color and finish in line and level, Including all fixing asseccories, Drilling, Fabricating, Scaffolding all labour etc. complete. Spec. No. As directed by Engineer in Charge.
| FIRST FLOOR | 5.7 | Sqm
10 | Providing and Fixing Acrylic Signage Board On Provided Base Of Aluminum Panel Sheet English Or Marathi of approved color and finish in line and level, Including all fixing asseccories, Drilling, Fabricating, Scaffolding all labour etc. complete. Spec. No. As directed by Engineer in Charge.
| GROUND FLOOR | 33.76 | Sqm
11 | Providing And Paisting Mural Art Wall Painting of approved Quality and finish in line and level, Including all fixing asseccories, Scaffolding And all Labour etc. complete. Spec. No. As directed by Engineer in Charge.
| FIRST FLOOR | 18 | Sqm
12 | Providing and fixing in position PVC Drain Channel For Floor Drain Size Of Length 500mm Width 200mm And Depth 175mm With And Reinforced PVC Grid Cover Size Of Length 500mm Width 200mm with necessary fixtures and fitting including making joint & necessary fittings and tested etc. complete. Spec. No. As directed by Engineer in charge. ( ASTRAL CAT. NO. CSA200 AND CGRN20SG )
| GROUND FLOOR | 243.51 | Rmt
Total Civil works Amt (A)
B | FIRE FIGHTING
13 | PUMP (Electrically Driven)
Supplying, installing, testing & commissioning of electric driven, suitable for autometic operation of horizontal single stage centrifugal type synchoronous speed of 2900 rpm, TEFC conforming to IP-55 & flexible coupling gaurd mounted on a common structural base plate with 150mm dia gun metal pressure gauges with isolation cock and piping, suitable vibration elimination pads of approved design for pump foundation, motor to be suitable for 415 volts, 3 phase, 50 cycles AC.Pump shall be designed in such a way that any case drop in the pressure main fire or diesel pump/Pump will be started automatically and there shall be provision of to run the pump in auto as well as manual mode.
| Capacity 2280 LPM at 7 Kg/cm2 delivery pressure for Fire Hydrant / Sprinkler Network. | 1 | Each
14 | Pumps (Diesel) Engine Driven | 1 | Each
Supplying, installing, testing and commissioning of horizontal single stage centrifugal pumping set with CI volute and bronze impeller with mechanical seals directly coupled to automatic Diesel Engine complete with all ccessories like self starting by means of Battery powered electric starter motor, oil bath air cleaner, exhaust silencer etc. complete in all respects. The engine & the pump will be mounted on common base plate on anti-vibration mountings 2200 LPM-56 MTR Head
15 | Control Panel (Engine Driven Pump) | 1 | Set
Supplying, erecting, testing and commissioning cubicle pattern electrical control panel (out door) made of 14 SWG MS sheet duly painted with powder coated comprising of the following:
24 Volts 120 AH capacity battery set.
15 Amps battery charger with Tricke and boost facility.
0-32 Volts votlmeter.
0-15 Amps ammeter.
Auto-starting contactor with relay.
Auto/Manual selector switch with push button for manual start.
16 | Oil Tank | 1 | Set
Supplying, fixing and commissioning 500 ltrs. capacity including first fill of 500 ltrs high speed diesel oil in 16 SWG MS steel oil tank with manhole cover, glass gauge, inlet and outlet connections with gate valves, drain plug, GI piping between tank and engine vent pipe with wire mesh etc. duly painted and mounted on suitable MS angle staging to maintain gravity flow of oil.
17 | Exhaust Piping | 1 | Rmt
Supplying, erecting and commissioning additional exhaust piping with heat resistance asbestos rope insulation wrapped all along the pipe including a cowl at the top with necessary MS clamps on walls/ceiling.
18 | Fire Pump Panel (Electrical) | 1 | Set
Suppling, erecting, testing and commissioning cubicle pattern electrical control panel made of 14 SWG MS Sheet duly painted with enamel paint, comprising of the following:
Incoming
1 No, 400Amps FP MCCB (50 KA)
Bus Bars
1 Set 3 Phase, 4 wire busbar 400 Amps Aluminium conductor, duly sleeved in PVC colour coded sleeves.
Outgoings
2 Nos 150 A TP MCCB withneutral link (25 KA)
1 Nos 63 A TP MCCB with neutral link (25 KA)
2 No. Star Delta starter with overload relay suitable for 70 HP.
1 No. Dol starter with overload relay suitable for 10 HP.
Metering
1 Set RYB phase indication lamps with toggle suitable and protection fuses.
1 No. 0-500 volts, 96mm square with with MCB.
1 No. 0-400 Amps Ammeter of 96mm square with CT's
1 No. 96sqmm energy meter with CT's
19 | Supplying and installing 32 mm GI C Class ERW Pipe | 1 | Rmt
20 | Supplying and installing 40 mm GI C Class ERW Pipe | 1 | Rmt
21 | Supplying and installing 65 mm GI C Class ERW Pipe | 1 | Rmt
22 | 150mm dia. Installation Control Valve assembly comprissing of vertical wet alarm valve, including the cost of 150 mm dia butterfly valve, hydraulic alarm motor & gong, 15mm dia. Test valve, 50mm dia. Drain valve and all necessary trimming connections including 2 nos. pressure gauges as per manufacturer's catalogue (UL / FM approved ). | 1 | Each
Total Amount of Mechanical works (B)
C | INTERNAL, EXTERNAL ELECTRIFICATION
23 | 10W LED Mirror light of Wipro Make Cat No. D531065 GARNET BATTEN | 1 | Each
24 | Supplying and fixing 32A 3∅ Industrial Power Socket with enclosure | 1 | Each
25 | Supplying and fixing 20A 1∅ Industrial Power Socket with enclosure | 1 | Each
26 | Supply installation testing and commissiong of 6 W public area ceiling speakers 85 dBA @ 3m @ lowest setting complete with GI backboX. | 1 | Each
27 | MAIN LT PANEL
| Supplying, installing, testing and commissioning cubicle type free floor mounted front operated panels made out of 14 SWG powder coated sheet steel, PVC colour coded aluminium bus bar, 75 x 6 Sq.mm aluminium earth tape from end to end of the panel, consisting of the following, all as per single line diagram. (G.A. drawing of panel to be approved before fabrication) Site inspection required before despatching the panel at site. | 1 | Each
All Incoming and Outgoing ACBs/MCCB's shall have Ics=Icu=Icw=95/65/50/35/25KA minimum having microprocessor based release trip with O/C, S/C, E/F protection and ON/OFF/TRIP indication for each.
All MCCB's shall have with rotary operating mechanism and ON/OFF indication for each.
Incoming
1000 Amps, 415 Volts, 4 Pole, 50Hz, ACB 50KA
Bus bars
1 Set of 1000 Amps, 415 Volts, 50 Hz, 3 phase, 4 wire colour coded Al. bus bars.
Instruments
1 No 0-500 Volts, Digital voltmeter with built in selector switch and protection fuses.
1 No 0-1000 Amps, Digital ammeter with built in selector switch and matching CT's .
1 Set of RYB phase indicating lamps (LED).
1 Set red & green (ON, OFF) indicating lamps (LED) for incomer.
1 Set of multification KWH meter (Suitable CT/PT)
Outgoing
02 Nos.315A TP MCB,35 KA
01 Nos.200A TP MCB,25 KA
01 Nos.160A TP MCB,25 KA
02 Nos.100A TP MCB,25 KA
04 Nos. 63A TP MCB, 10 KA
01 Nos. 50A TP MCB, 10 KA
01 Nos. 40A TP MCB, 10 KA
02 Nos. Vaccant
02 Nos. Spare
28 | Supplying, installing, testing and commissioning cubicle type free floor mounted front operated panels made out of 14 SWG powder coated sheet steel, PVC colour coded aluminium bus bar, 75 x 6 Sq.mm aluminium earth tape from end to end of the panel, consisting of the following, all as per single line diagram. (G.A. drawing of panel to be approved before fabrication) Site inspection required before despatching the panel at site. | 1 | Each
All Incoming and Outgoing ACBs/MCCB's shall have Ics = Icu = Icw = 95 / 65 / 50 / 35 / 25KA minimum having microprocessor based release trip with O/C, S/C, E/F protection and ON/OFF/TRIP indication for each.
All MCCB's shall have with rotary operating mechanis and ON/OFF indication for each.
Incoming
160 Amps, 415 Volts, 4 Pole, 50Hz, MCCB 25KA
Bus bars
1 Set of 160 Amps, 415 Volts, 50 Hz, 3 phase, 4 wire colour coded Al. bus bars.
Instruments
1 No 0-500 Volts, Digital voltmeter with built in selector switch and protection fuses.
1 No 0-160 Amps, Digital ammeter with built in selector switch and matching CT's .
1 Set of RYB phase indicating lamps (LED).
1 Set red & green (ON, OFF) indicating lamps (LED) for incomer.
1 Set of multification KWH meter (Suitable CT/PT)
Outgoing
01 Nos.63A TP MCB,10 KA
05 Nos.40A TP MCB,10 KA
06 Nos.32A TP MCB,10 KA
02 Nos. Spare
29 | CAPACITOR PANEL (150 KVAR) | 1 | Each
Incoming
01 Nos. 250 Amps, TP MCCB 35KA
Bus bar
1 set of 250 Amps, 415 volts, 50 Hz, 3 phase, 4 wire colour coded aluminium bus bars.
Outgoing
02 Nos. 125 Amps, TP MCCB with isolable neutral
01 Nos. 70 Amps, TP MCB with isolable neutral
01 Nos. 50 Amps, TP MCB with isolable neutral
03 Nos. 32 Amps, TP MCB with isolable neutral
02 Nos. 50 KVAR 3 phase 415 V capacitor
01 Nos. 25 KVAR 3 phase 415 V capacitor
01 Nos. 10 KVAR 3 phase 415 V capacitor
03 Nos. 5 KVAR 3 phase 415 V capacitor
1 set red & green (on/off) indication for each contactor.
Sets on/off push buttons for manual operation
1 No. 12-14 stage APFCR and allied control wiring in-built power factor meter.
1 No. automanual selector switch.
Note- Each capacitor bank shall have facility of switiching on individually in manual mode independent of APCR relay or in auto mode through APCR relay. Few contactor shall be kept for fixed operation.
30 | External Lighting DB (Feeder Pilar) | 1 | Each
Incoming
1 No. 63 Amps, FP RCBO, 415 volts, 3 phase, 50 Hz (100 mA Sensitivity).
1 No. 60 Amps, FP contactor with auxiliary contacts. The contactor to be controlled by Timer through an Auto/Manual Selector switch. Timer shall be 24 hrs programmable.
Outgoing
4 Nos 32 Amps, TPN MCB, 415 volts, 3 phase, 50 Hz.
Bus bar
1 set 63 Amps, 415 volts, 3 phase 4 wire colour coded copper bus bars.
Neutral Link
Suitable for above outgoings separate for each phase.
Earthing Bus
Suitable for above outgoings separate for each phase.
LIGHTING ARRESTER
31 | Supply, installation, testing of Transducer type Building lightning arrester "EARLY STREAMER" to cover protection radius of 65.0 mtr. with 5mtr stem and fixing arrangement. (Indelec or Eqvt.). Required installation/ mounting details shall be submitted prior to installation. | 1 | NOS.
32 | Supply, Installation, testing of Copper 5 spikes Building lightning arrester with stem and fixing arrangement. | 1 | NOS.
33 | Supply, installation, testing of disconnecting link box for lightning down conductor at 1 mtr. from GL with SMC insulator and Gunmetal 50 x 6 mm disconnecting link. | 1 | NOS.
CC TV SURVEILLANCE
34 | Supply, Installation, Testing & Commissioning of 1/3", CCD type, Indoor application Colour Dome camera with 540 TVL and lens 4 to 9 mm focal lens, viewing angle wide Wide: 98.5º x 75.3º (H x V). | 1 | NOS.
35 | Supply, installation, testing & commissioning 4 channel Digital Video Recorder with capacity of 1TB built in Hard disk, and same shall be having the capacity to have analog and SVGA output, shall be with TCP/ IP connectivity. | 1 | NOS.
36 | Supply, installation, testing & commissioning of 21" Hi resolution Colour Monitor | 1 | NOS.
37 | RG 59 Coaxial Video Cable in 19mm PVC conduit with all accessories. | 1 | Rmt
38 | Supply and laying of 3 Core x 1.5 Sq.MM copper conductors, power cable in 19mm dia PVC conduits for Power Supply for the Dome Cameras. | 1 | Rmt
Total Amount of Electrical works (c)
TOTAL AMOUNT (A+B+C)